## ITP
N.J Devani Builders Pvt.Ltd |  |  | ITP No. : NJDBPL-ISBL-ITP-CS:001 |  |  | Inspection and Test Plan For General Requirements-Civil Works
Rev No. : 01
Date : 30.09.2012
Sheet No. : 02 OF 02
Area :- ISBL Contractor : N.J.Devani Builders Pvt.Ltd.
Building Name / Description - Civil Works For Construction of Sub Station cum Control Building. Work Order No. : 230068628
8 | Inspection and Test Plan For General Requirements-Civil Works
Sr. | Activity Description |  |  | Controlling Document | Acceptance criteria | Verifying Forms | Contractor | Reliance
[8 empty] | Construction |  | QMD | O&M/CES
8.1 | Perform a kickoff meeting to discuss Attachment- E contents and requirements |  |  | Attchment -E | __ | MOM | H | H |  | H | S
8.2 | Perform a Pre-construction walk down on location |  |  | Contractor Scope of Work | __ | MOM | H | H |  | S | S
8.3 | Obtain necessary JSA Prior to start of work. And Conduct Safety Tool Box Meeting Prior to Start of Work. |  |  | Job Specific JSA | Require safe work permits | Applicable JSA Record | H | H |  | DR | S
8.4 | Verify that Concrete Supplier and Mix designs are Approved for use on this Project. |  |  | Project Specification Approved Procedures Codes & Standards | Project Specification, Approved Drawings & Mix Design | CMTL Approved Design Mix and Past Concrete Records | H | H |  | H | W% (CES)
8.5 | Hot Weather Concreting Requirements are to be reviewed in detail during the Alignment Meeting. |  |  | Project Specification Approved Procedures Codes & Standards | Project Specification | Concrete Receival Inspection Record | H | H |  | S | S
8.6 | Verify that stacking area is in accordance project instruction including proper dunnage for precast elements. |  |  | Project Specification | Project Specification | Visual Inspection | H | H |  | S | S
8.7 |  | Notification to Security and plan on spotters on site is required to assure proper staging of trucks as load of concrete during a pour are under Strict time constraints. |  | Good Practice | Site Safety and Security requirements | __ | H | H |  | DR | S
| N.J.Devani Builders PVT.LTD Engineer |  | Reliance Construction Engineer |  | Reliance QMD |  |  | Reliance O&M/CES
|  |  | Discipline | Lead
Date
Name
Signature
N.J Devani Builders Pvt.Ltd |  |  | ITP No. : NJDBPL-ISBL-ITP-CS:002 |  |  | Inspection and Test Plan For Concrete Paving
Rev No. : 02
Date : 16.07.2013
Sheet No. : 02 OF 03
Area :- ISBL Contractor : N.J.Devani Builders Pvt.Ltd.
Building Name / Description - Civil Works For Construction of Sub Station cum Control Building. Work Order No. : 230068628
5 | Inspection and Test Plan For Concrete Paving
Sr. | Activity Description |  |  | Controlling Document | Acceptance criteria | Verifying Forms | Contractor | Reliance
[8 empty] | Construction |  | QMD | O&M/CES
[8 empty] | Disc | Lead
5.1 | Check sub-base compaction. |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-006 | As per approved drawings & applicable Specification - 10080-1-SS-CS-006 | EPCMD 2QM00FMTCS007 | H | H |  | S | S
5.2 | Pre-Pour inspections. |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS011 | H | H |  | S | S
5.3 | Release for Concrete Manufacture. (Pour Card) |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS015 | H | H |  | S | S
5.4 | Concrete Receival Inspection & Testing for slump, temperature (prior to placement). |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS010 / 009 | H | W |  | S | S
5.5 | Concrete cube sampling & testing at CMTL (Civil Material Testing Laboratory). |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS009 | H | W |  | Sampling -S Testing-H | S
5.6 | Concrete Placement, Finishing & Curing. |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS008 | H | S |  | S | S
5.7 | Check surface levels, coordinates within tolerances. |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | Survey report | H | H |  | S | S
| N.J.Devani Builders PVT.LTD Engineer |  | Reliance Construction Engineer |  | Reliance QMD |  |  | Reliance O&M/CES
|  |  | Discipline | Lead
Date
Name
Signature
N.J Devani Builders Pvt.Ltd |  |  | ITP No. : NJDBPL-ISBL-ITP-CS:002 |  |  | Inspection and Test Plan For Concrete Paving
Rev No. : 02
Date : 16.07.2013
Sheet No. : 03 OF 03
Area :- ISBL Contractor : N.J.Devani Builders Pvt.Ltd.
Building Name / Description - Civil Works For Construction of Sub Station cum Control Building. Work Order No. : 230068628
Sr. | Activity Description |  |  | Controlling Document | Acceptance criteria | Verifying Forms | Contractor | Reliance
[8 empty] | Construction |  | QMD | O&M/CES
[8 empty] | Disc | Lead
5.8 | Inspection of expantion & Contraction joints & Sealant application |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS054 | H | H |  | S | S
5.9 | Check markings applied as required. |  |  | Approved Drawings | Approved Drawings | ---- | H | W |  | S | S
5.1 | Check concrete curbs / bumps / camber installed as per drawing. |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | Level record | H | W |  | S | S
| N.J.Devani Builders PVT.LTD Engineer |  | Reliance Construction Engineer |  | Reliance QMD |  |  | Reliance O&M/CES
|  |  | Discipline | Lead
Date
Name
Signature
N.J Devani Builders Pvt.Ltd |  |  | ITP No. : NJDBPL-ISBL-ITP-CS:003 |  |  | Inspection and Test Plan For Manhole Construction, Erection & Testing
Rev No. : 03
Date : 30.09.2013
Sheet No. : 02 OF 03
Area :- ISBL Contractor : N.J.Devani Builders Pvt.Ltd.
Building Name / Description - Civil Works For Construction of Sub Station cum Control Building. Work Order No. : 230068628
3 | Inspection and Test Plan For Manhole Construction, Erection & Testing
Sr. | Activity Description |  |  | Controlling Document | Acceptance criteria | Verifying Forms | Contractor | Reliance
[8 empty] | Construction |  | QMD | O&M/CES
[8 empty] | Disc | Lead
3.1 | Excavation , Base Compaction and Blinding Concrete. |  |  | As per approved drawings & applicable Specification | As per approved drawings & applicable Specification | EPCMD 2QM00FMTCS003 EPCMD 2QM00FMTCS005 | H | H | S | S | S
3.2 | Pre-pour inspections (Rebar, formwork, embedded items etc.) |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS014 | H | H | H | S | S
3.3 | Check Proper installation of Hydrophilic bars in Contruction Joint as per vendor Specified Method. |  |  | As per approved drawings & applicable Specification | As per approved drawings & applicable Specification - | EPCMD 2QM00FMTCS054 | H | H | S | S | S
3.4 | Release for Concrete manufacture and supply (Pour Card) |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS015 | H | H | H | S | S
3.5 |  | Concrete Receival Inspection and Sampling for slump, temperature (Prior to placement) |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS010 | H | W | S | S | S
3.6 | Concrete cube sampling & testing at CMTL (Civil Material Testing Laboratory) |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS009 | H | W | S | Sampling -S Testing-H | S
3.7 | Concrete Placement, Finishing and Curing |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS008 | H | S | S | S | S
| N.J.Devani Builders PVT.LTD Engineer |  | Reliance Construction Engineer |  | Reliance QMD |  |  | Reliance O&M/CES
|  |  | Discipline | Lead
Date
Name
Signature
N.J Devani Builders Pvt.Ltd |  |  | ITP No. NJDBPL-ISBL-ITP-CS:003 |  |  | Inspection and Test Plan For Manhole Construction, Erection & Testing
Rev No. : 03
Date : 30.09.2013
Sheet No. : 03 OF 03
Area :- ISBL Contractor : N.J.Devani Builders Pvt.Ltd.
Building Name / Description - Civil Works For Construction of Sub Station cum Control Building. Work Order No. : 230068628
Sr. | Activity Description |  |  | Controlling Document | Acceptance criteria | Verifying Forms | Contractor | Reliance
[8 empty] | Construction |  | QMD | O&M/CES
[8 empty] | Disc | Lead
3.8 | Concrete Surface Inspections and Repairs |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS043 | H | H | S | S | S
3.9 | Leak Testing Manhole For Impermeability |  |  | As per approved drawings & applicable Specification | As per approved drawings & applicable Specification - | EPCMD 2QM00FMTCS025 | H | H | S | S | W% (CES)
3.1 | Precast Placement and realease for Backfill. ( Coordinates to be check by Survey) |  |  | As per approved drawings & applicable Specification | As per approved drawings & applicable Specification | EPCMD 2QM00FMTCS053 | H | W | S | S | S
3.11 |  | Backfill and compaction around Manhole. |  | As per approved drawings & applicable Specification | As per approved drawings & applicable Specification | EPCMD 2QM00FMTCS004 | H | W | S | S | S
| N.J.Devani Builders PVT.LTD Engineer |  | Reliance Construction Engineer |  | Reliance QMD |  |  | Reliance O&M/CES
|  |  | Discipline | Lead
Date
Name
Signature
N.J Devani Builders Pvt.Ltd |  |  | ITP No. : NJDBPL-ISBL-ITP-CS:004 |  |  | Inspection And Test Plan For Structural Concrete
Rev No. : 03
Date : 16.07.2013
Sheet No. : 02 OF 03
Area :- ISBL Contractor : N.J.Devani Builders Pvt.Ltd.
Building Name / Description - Civil Works For Construction of Sub Station cum Control Building. Work Order No. : 230068628
2 | Inspection And Test Plan For Structural Concrete
Sr. | Activity Description |  |  | Controlling Document | Acceptance criteria | Verifying Forms | Contractor | Reliance
[8 empty] | Construction |  | QMD | O&M/CES
[8 empty] | Disc | Lead
2.1 | Pre-pour inspections (Rebar, formwork, embedded items etc.) |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS014 | H | H | H | S | S
2.2 | Release for Concrete manufacture and supply (Pour Card) |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS015 | H | H | H | S | S
2.3 | Concrete Receival Inspection and Sampling for slump, temperature (Prior to placement) |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 |  | H | W | S | S | S
| Normal concrete work : |  |  |  |  | EPCMD 2QM00FMTCS010
| Self compacting concrete : |  |  |  |  | EPCMD 2QM00FMTCS101
2.4 | Concrete cube sampling & testing at CMTL (Civil Material Testing Laboratory) |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS009 | H | W | S | Sampling -S Testing-H | S
| N.J.Devani Builders PVT.LTD Engineer |  | Reliance Construction Engineer |  | Reliance QMD |  |  | Reliance O&M/CES
|  |  | Discipline | Lead
Date
Name
Signature
N.J Devani Builders Pvt.Ltd |  |  | ITP No. : NJDBPL-ISBL-ITP-CS:004 |  |  | Inspection And Test Plan For Structural Concrete
Rev No. : 03
Date : 16.07.2013
Sheet No. : 03 OF 03
Area :- ISBL Contractor : N.J.Devani Builders Pvt.Ltd.
Building Name / Description - Civil Works For Construction of Sub Station cum Control Building. Work Order No. : 230068628
Sr. | Activity Description |  |  | Controlling Document | Acceptance criteria | Verifying Forms | Contractor | Reliance
[8 empty] | Construction |  | QMD | O&M/CES
[8 empty] | Disc | Lead
2.5 | Concrete Placement, Finishing and Curing |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS008 | H | S | S | S | S
2.6 | Concrete Surface Inspections and Repairs |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS043 | H | H | S | S | S
2.7 | Inspection of contraction and Expansion Joint |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS054 | H | H | S | S | S
2.8 | Water proofing treatment as applicable |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-011 | As per approved drawings & applicable Specification - 10080-1-SS-CS-011 | EPCMD 2QM00FMTCS042 | H | H | S | S | S
2.9 | Release for structural steel / equipment erection. |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS006 | H | H | S | S | S
| N.J.Devani Builders PVT.LTD Engineer |  | Reliance Construction Engineer |  | Reliance QMD |  |  | Reliance O&M/CES
|  |  | Discipline | Lead
Date
Name
Signature
N.J Devani Builders Pvt.Ltd |  |  | ITP No. : NJDBPL-ISBL-ITP-CS:005 |  |  | Inspection And Test Plan For Equipment Foundation
Rev No. : 03
Date : 16.07.2013
Sheet No. : 02 OF 04
Area :- ISBL Contractor : N.J.Devani Builders Pvt.Ltd.
Building Name / Description - Civil Works For Construction of Sub Station cum Control Building. Work Order No. : 230068628
1 | Inspection And Test Plan For Equipment Foundation
Sr. | Activity Description |  |  | Controlling Document | Acceptance criteria | Verifying Forms | Contractor | Reliance
[8 empty] | Construction |  | QMD | O&M/CES
[8 empty] | Disc | Lead
1.1 | Compliance of the general requirement for Civil filed execution work |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-006 | As per approved drawings & applicable Specification - 10080-1-SS-CS-006 | EPCMD 2QM 00 ITP CS040 | H | H | S | DR | DR
1.2 | Pre Excavation setting out and checks. |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-006 | As per approved drawings & applicable Specification - 10080-1-SS-CS-006 | EPCMD 2QM00FMTCS002 | H | H | S | S | S
1.3 | Excavation and base confirmation. |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-006 | As per approved drawings & applicable Specification - 10080-1-SS-CS-006 | EPCMD 2QM00FMTCS003 | H | H | S | S | S
1.4 | Blinding concrete placement and curing. |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS005 | H | S | S | S | S
1.5 | Pre-pour inspections (Rebar, formwork, embedded items etc.) |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS014 | H | H | H | S | S
1.6 | Release for Concrete manufacture and supply (Pour Card) |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS015 | H | H | H | S | S
| N.J.Devani Builders PVT.LTD Engineer |  | Reliance Construction Engineer |  | Reliance QMD |  |  | Reliance O&M/CES
|  |  | Discipline | Lead
Date
Name
Signature
N.J Devani Builders Pvt.Ltd |  |  | ITP No. : NJDBPL-ISBL-ITP-CS:005 |  |  | Inspection And Test Plan For Equipment Foundation
Rev No. : 03
Date : 16.07.2013
Sheet No. : 03 OF 04
Area :- ISBL Contractor : N.J.Devani Builders Pvt.Ltd.
Building Name / Description - Civil Works For Construction of Sub Station cum Control Building. Work Order No. : 230068628
Sr. | Activity Description |  |  | Controlling Document | Acceptance criteria | Verifying Forms | Contractor | Reliance
[8 empty] | Construction |  | QMD | O&M/CES
[8 empty] | Disc | Lead
1.7 | Concrete Receival Inspection and Sampling for slump, temperature (Prior to placement) |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 |  | H | W | S | S | S
| Normal concrete work : |  |  |  |  | EPCMD 2QM00FMTCS010
| Self compacting concrete : |  |  |  |  | EPCMD 2QM00FMTCS101
1.8 | Concrete cube sampling & testing at CMTL (Civil Material Testing Laboratory) |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS009 | H | W | S | Sampling -S Testing-H | S
1.9 | Concrete Placement, Finishing and Curing |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS008 | H | W | S | S | S
1.1 | Concrete Surface Inspections and Repairs |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS043 | H | H | S | S | S
1.11 | Waterproof coating. (If applicable) |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-011 | As per approved drawings & applicable Specification - 10080-1-SS-CS-011 | EPCMD 2QM00FMTCS020 | H | H | S | S | S
1.12 | Waterproof membrane. (If applicable) |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-011 | As per approved drawings & applicable Specification - 10080-1-SS-CS-011 | EPCMD 2QM00FMTCS042 | H | H | S | S | S
| N.J.Devani Builders PVT.LTD Engineer |  | Reliance Construction Engineer |  | Reliance QMD |  |  | Reliance O&M/CES
|  |  | Discipline | Lead
Date
Name
Signature
N.J Devani Builders Pvt.Ltd |  |  | ITP No. : NJDBPL-ISBL-ITP-CS:005 |  |  | Inspection And Test Plan For Equipment Foundation
Rev No. : 03
Date : 16.07.2013
Sheet No. : 04 OF 04
Area :- ISBL Contractor : N.J.Devani Builders Pvt.Ltd.
Building Name / Description - Civil Works For Construction of Sub Station cum Control Building. Work Order No. : 230068628
Sr. | Activity Description |  |  | Controlling Document | Acceptance criteria | Verifying Forms | Contractor | Reliance
[8 empty] | Construction |  | QMD | O&M/CES
[8 empty] | Disc | Lead
1.13 | Backfill and compaction to foundations. |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-006 | As per approved drawings & applicable Specification - 10080-1-SS-CS-006 | EPCMD 2QM00FMTCS004 EPCMD 2QM00FMTCS021 | H | W | S | S | S
1.14 | Filling with fill crete material (If applicable) |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-006 | As per approved drawings & applicable Specification - 10080-1-SS-CS-006 | EPCMD 2QM00FMTCS073 | H | S | S | S | S
1.15 | Release for hand over to equipment erection. |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS006 | H | H | S | S | S
| N.J.Devani Builders PVT.LTD Engineer |  | Reliance Construction Engineer |  | Reliance QMD |  |  | Reliance O&M/CES
|  |  | Discipline | Lead
Date
Name
Signature
N.J Devani Builders Pvt.Ltd |  |  | ITP No. : NJDBPL-ISBL-ITP-CS:006 |  |  | Inspection and Test Plan For Excavation, Base Compaction & Blinding Concrete
Rev No. : 02
Date : 16.07.2013
Sheet No. : 02 OF 02
Area :- ISBL Contractor : N.J.Devani Builders Pvt.Ltd.
Building Name / Description - Civil Works For Construction of Sub Station cum Control Building. Work Order No. : 230068628
4 | Inspection and Test Plan For Excavation, Base Compaction & Blinding Concrete
Sr. | Activity Description |  |  | Controlling Document | Acceptance criteria | Verifying Forms | Contractor | Reliance
[8 empty] | Construction |  | QMD | O&M/CES
[8 empty] | Disc | Lead
4.1 | Excavation setting out and checks. |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-006 | As per approved drawings & applicable Specification - 10080-1-SS-CS-006 | EPCMD 2QM00FMTCS002 EPCMD 2QM00FMTCS003 Survey report | H | W |  | S | S
4.2 | Earthwork Filling and Compaction. |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-006 | As per approved drawings & applicable Specification - 10080-1-SS-CS-006 | EPCMD 2QM00FMTCS004 | H | W |  | S | S
4.3 | Blinding concrete placement and curing. |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-006 | As per approved drawings & applicable Specification - 10080-1-SS-CS-006 | EPCMD 2QM00FMTCS005 | H | W |  | S | S
| N.J.Devani Builders PVT.LTD Engineer |  | Reliance Construction Engineer |  | Reliance QMD |  |  | Reliance O&M/CES
|  |  | Discipline | Lead
Date
Name
Signature
N.J Devani Builders Pvt.Ltd |  |  | ITP No. : NJDBPL-ISBL-ITP-CS:007 |  |  | Inspection And Test Plan For INSTALLATION OF DOORS AND WINDOWS
Rev No. : 01
Date : 26.12.2012
Sheet No. : 02 OF 02
Area :- ISBL Contractor : N.J.Devani Builders Pvt.Ltd.
Building Name / Description - Civil Works For Construction of Sub Station cum Control Building. Work Order No. : 230068628
6 | Inspection And Test Plan For INSTALLATION OF DOORS AND WINDOWS
Sr. | Activity Description |  |  | Controlling Document | Acceptance criteria | Verifying Forms | Contractor | Reliance
[8 empty] | Construction |  | QMD | O&M/CES
[8 empty] | Disc | Lead
6.1 | Check frames & shutters of doors & windows conforming requirement of dimention,grooves,pannels & anyother specified |  |  | Approved Drawing / Specification:10080-1-SS-CS-012 Rev 00 | Approved Drawing / Specification:10080-1-SS-CS-012 Rev 00 | Manufactures T.C/Party certificates | H | H | S | S | S
6.2 | Check the material of the frame & shutter is conforming & free fro any visual damages |  |  | Approved Drawing / Specification:10080-1-SS-CS-012 Rev 00 | Approved Drawing / Specification:10080-1-SS-CS-012 Rev 00 | EPCMD-2QMOOFMTCS001 | H | w | S | S | S
6.3 | Check the position,size andnumbers of holdfast |  |  | Approved Drawing / Specification:10080-1-SS-CS-012 Rev 00 | Approved Drawing / Specification:10080-1-SS-CS-012 Rev 00 | EPCMD-2QMOOFMTCS001 | H | w | S | S | S
6.4 | Plum the frame to ensure its upright,and free from twist |  |  | Approved Drawing / Specification:10080-1-SS-CS-012 Rev 00 | Approved Drawing / Specification:10080-1-SS-CS-012 Rev 00 | EPCMD-2QMOOFMTCS001 | H | w | S | S | S
6.5 | Check whether sufficient precautions are taken to avoid distortion of the frame during installation. |  |  | Approved Drawing / Specification:10080-1-SS-CS-012 Rev 00 | Approved Drawing / Specification:10080-1-SS-CS-012 Rev 00 | EPCMD-2QMOOFMTCS001 | H | w | S | S | S
6.6 | Check proper sealent/screw/mortar as applicable is applied properly after fitting of frame |  |  | Approved Drawing / Specification:10080-1-SS-CS-012 Rev 00 | Approved Drawing / Specification:10080-1-SS-CS-012 Rev 00 | EPCMD-2QMOOFMTCS001 | H | w | S | S | S
6.7 | Check correctness in potion & installationof hinges |  |  | Approved Drawing / Specification:10080-1-SS-CS-012 Rev 00 | Approved Drawing / Specification:10080-1-SS-CS-012 Rev 00 | EPCMD-2QMOOFMTCS001 | H | w | S | S | S
6.8 | Check Orientation of Doors & Frames |  |  | Approved Drawing / Specification:10080-1-SS-CS-012 Rev 00 | Approved Drawing / Specification:10080-1-SS-CS-012 Rev 00 | EPCMD-2QMOOFMTCS001 | H | H | S | S | S
6.9 | Swing of Doors are free from any disturbunces |  |  | Approved Drawing / Specification:10080-1-SS-CS-012 Rev 00 | Approved Drawing / Specification:10080-1-SS-CS-012 Rev 00 | EPCMD-2QMOOFMTCS001 | H | H | S | S | S
6.1 | Check installation of required fittings conforming to requirement. |  |  | Approved Drawing / Specification:10080-1-SS-CS-012 Rev 00 | Approved Drawing / Specification:10080-1-SS-CS-012 Rev 00 | EPCMD-2QMOOFMTCS001 | H | H | S | S | S
| Contractor Engineer |  | Reliance Construction Engineer |  | Reliance QMD |  |  | Reliance O&M/CES
|  |  | Discipline | Lead
Date
Name
Signature
N.J Devani Builders Pvt.Ltd |  |  | ITP No. : NJDBPL-ISBL-ITP-CS:008 |  |  | Inspection and Test Plan For Concrete Work of Water Retaining Structure
Rev No. : 01
Date : 16.07.2013
Sheet No. : 02 OF 04
Area :- ISBL Contractor : N.J.Devani Builders Pvt.Ltd.
Building Name / Description - Civil Works For Construction of Sub Station cum Control Building. Work Order No. : 230068628
7 | Inspection and Test Plan For Concrete Work of Water Retaining Structure
Sr. | Activity Description |  |  | Controlling Document | Acceptance criteria | Verifying Forms | Contractor | Reliance
[8 empty] | Construction |  | QMD | O&M/CES
[8 empty] | Disc | Lead
7.1 | Excavation setting out and checks. |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-006 | As per approved drawings & applicable Specification - 10080-1-SS-CS-006 | EPCMD 2QM00FMTCS002 | H | H | S | S | S
7.2 | Base compaction and blinding preparation. |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-006 | As per approved drawings & applicable Specification - 10080-1-SS-CS-006 | EPCMD 2QM00FMTCS003 | H | S | S | S | S
7.3 | Blinding concrete placement and curing. |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS005 | H | S | S | S | S
7.4 | Check for proper installation of (1) Hydrophilic bar in construction joint and (2) Expansion Joints as per vendor specified method. |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS054 | H | H | S | S | S
7.5 | Pre-pour inspections. (Rebar, formwork, embedded items etc.) |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS014 | H | H | H | S | S
7.6 | Release for Concrete manufacture and supply (Pour Card). |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS015 | H | H | H | S | S
| N.J.Devani Builders PVT.LTD Engineer |  | Reliance Construction Engineer |  | Reliance QMD |  |  | Reliance O&M/CES
|  |  | Discipline | Lead
Date
Name
Signature
N.J Devani Builders Pvt.Ltd |  |  | ITP No. : NJDBPL-ISBL-ITP-CS:008 |  |  | Inspection and Test Plan For Concrete Work of Water Retaining Structure
Rev No. : 01
Date : 16.07.2013
Sheet No. : 03 OF 04
Area :- ISBL Contractor : N.J.Devani Builders Pvt.Ltd.
Building Name / Description - Civil Works For Construction of Sub Station cum Control Building. Work Order No. : 230068628
Sr. | Activity Description |  |  | Controlling Document | Acceptance criteria | Verifying Forms | Contractor | Reliance
[8 empty] | Construction |  | QMD | O&M/CES
[8 empty] | Disc | Lead
7.7 | Concrete Receival Inspection and Sampling for slump, temperature (Prior to placement). |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 |  | H | W | S | S | S
| Normal concrete work : |  |  |  |  | EPCMD 2QM00FMTCS010
| Self compacting concrete : |  |  |  |  | EPCMD 2QM00FMTCS101
7.8 | Concrete cube sampling & testing at CMTL (Civil Material Testing Laboratory). |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS009 | H | W | S | Sampling -S Testing-H | S
7.9 | Concrete Placement, Finishing and Curing. |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS008 | H | W | S | S | S
7.1 | Grouting the tie rod cone & Concrete Surface Inspections and Repairs if any. |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS043 | H | H | S | S | S
7.11 | Waterproof coating. (If applicable) |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-011 | As per approved drawings & applicable Specification - 10080-1-SS-CS-011 | EPCMD 2QM00FMTCS020 / 042 | H | H | S | S | S
7.12 | Leak test as per applicable procedure. |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-011 | As per approved drawings & applicable Specification - 10080-1-SS-CS-011 | EPCMD 2QM00FMTCS096 | H | H | W | S | S
| N.J.Devani Builders PVT.LTD Engineer |  | Reliance Construction Engineer |  | Reliance QMD |  |  | Reliance O&M/CES
|  |  | Discipline | Lead
Date
Name
Signature
N.J Devani Builders Pvt.Ltd |  |  | ITP No. : NJDBPL-ISBL-ITP-CS:008 |  |  | Inspection and Test Plan For Concrete Work of Water Retaining Structure
Rev No. : 01
Date : 16.07.2013
Sheet No. : 04 OF 04
Area :- ISBL Contractor : N.J.Devani Builders Pvt.Ltd.
Building Name / Description - Civil Works For Construction of Sub Station cum Control Building. Work Order No. : 230068628
Sr. | Activity Description |  |  | Controlling Document | Acceptance criteria | Verifying Forms | Contractor | Reliance
[8 empty] | Construction |  | QMD | O&M/CES
[8 empty] | Disc | Lead
7.13 | Backfill and compaction to foundations. |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-006 | As per approved drawings & applicable Specification - 10080-1-SS-CS-006 | EPCMD 2QM00FMTCS004 EPCMD 2QM00FMTCS021 | H | W | S | S | S
7.14 | Release for structural steel / equipment erection. |  |  | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | As per approved drawings & applicable Specification - 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS006 | H | H | S | S | S
| N.J.Devani Builders PVT.LTD Engineer |  | Reliance Construction Engineer |  | Reliance QMD |  |  | Reliance O&M/CES
|  |  | Discipline | Lead
Date
Name
Signature
N.J Devani Builders Pvt.Ltd |  |  | ITP No. : NJDBPL-ISBL-ITP-CS:009 |  |  | Inspection and Test Plan For Construction of Building
Rev No. : 02
Date : 22.02.2017
Sheet No. : 02 OF 09
Area :- ISBL Contractor : N.J.Devani Builders Pvt.Ltd.
Building Name / Description - Civil Works For Construction of Sub Station cum Control Building. Work Order No. : 230068628
9 |  | Inspection and Test Plan For Construction of Building
Sr. | Activity Description |  |  | Controlling Document | Acceptance criteria | Verifying Forms | Contractor | Client
[8 empty] | Construction |  | QMD | O&M/CES
[8 empty] | Disc | Lead
1 | Site Clearance with necessary trial pits for soil classification |  |  | IS 1892 / 10042 | Site Clearance from authorized agency | Site Clearance Certificate | H | DR | DR | DR | DR
2 | Soil Investigation |  |  | Approved Drawing / applicable Procedure | IS 8009 / IS 1888 | Soil Investigation Report | H | DR | DR | DR | DR
3 | Area Survey & Grid Marking, Establishment of TBM (Temporary Bench Mark) |  |  | Approved Drawing / applicable Procedure | Approval Drawing/Standard Survey Norms | Survey Report | H | W | S | S | DR
4 | Excavation & Anti-termite treatment |  |  | Approved Drawing / Manufacturer Specification / Data Sheet | Approved Drawing / Manufacturer Specification / Data Sheet | EPCMD 2QM00FMTCS003 | H | S | S | S | S
5 | Blinding concrete |  |  | Approved Drawing / Specification | Approved Drawing / Specification | EPCMD 2QM00FMTCS005 | H | S | S | S | S
6 | Pre Pour Inspection : Shuttering, reinforcement work for foundations and super structure |  |  | Approved Drawing / Specification | Approved Drawing / Specification | EPCMD 2QM00FMTCS014 | H | H | H | S | S
7 | Concrete work for foundation and super structure |  |  | Approved Drawing / Specification | Approved Drawing / Specification No. : 10080-1-SS-CS-002 | EPCMD 2QM00FMTCS008 EPCMD 2QM00FMTCS015 EPCMD 2QM00FMTCS010 | H | H | S | S | S
| N.J.Devani Builders PVT.LTD Engineer |  | Reliance Construction Engineer |  | Reliance QMD |  |  | Reliance O&M/CES
|  |  | Discipline | Lead
Date
Name
Signature
N.J Devani Builders Pvt.Ltd |  |  | ITP No. : NJDBPL-ISBL-ITP-CS:009 |  |  | Inspection and Test Plan For Construction of Building
Rev No. : 06
Date : 22.02.2017
Sheet No. : 03 OF 09
Area :- ISBL Contractor : N.J.Devani Builders Pvt.Ltd.
Building Name / Description - Civil Works For Construction of Sub Station cum Control Building. Work Order No. : 230068628
Sr. | Activity Description |  |  | Controlling Document | Acceptance criteria | Verifying Forms | Contractor | Client
[8 empty] | Construction |  | QMD | O&M/CES
[8 empty] | Disc | Lead
8 | Sampling and testing of conrete cube |  |  | Approved Drawing / Procudure No. : EPCMD-2-QM00-JEP-CS-22 / Specification | Approved Drawing / Procudure No. : EPCMD-2-QM00-JEP-CS-22 / Specification | EPCMD 2QM00FMTCS009 | H | W | S | Sampling -S Testing-H | S
9 | Concrete surface repairing as applicable |  |  | Approved Drawing / Approved Repairing Procedure / Specification | Approved Drawing / Approved Repairing Procedure / Specification | EPCMD 2QM00FMTCS043 | H | H | S | S | S
10 |  | Masonary Work
10.1 | Check for Suitability of bricks/blocks, sand, water, cement etc. |  |  | Approved Drawing / Specification & EPCMD - 2 - QM00 - JEP - CS - 024 | Approved Drawing / Specification & EPCMD - 2 - QM00 - JEP - CS - 024 | Material test Report | H | H | DR | DR | DR
10.2 | Mortar batching with correct gauges and as per applicable mix proportion |  |  | Approved Drawing / Specification | Approved Drawing / Specification | EPCMD 2QM00FMTCS059 | H | W | S | S | S
10.3 | Construction of the masonary |  |  | Approved Drawing / Specification | Approved Drawing / Specification | EPCMD 2QM00FMTCS059 | H | S | S | S | S
10.4 | Curing of the masonary |  |  | Approved Drawing / Specification | Approved Drawing / Specification | EPCMD 2QM00FMTCS059 | H | S | S | S | S
11 | Flooring
11.1 | Back filling & Compaction below flooring |  |  | Approved Drawing / Procudure No. : EPCMD-2QM00-JEP-CS-026 / Specification | Approved Drawing / Procudure No. : EPCMD-2QM00-JEP-CS-026 / Specification | EPCMD 2QM00FMTCS004 | H | H | S | S | S
| Contractor Engineer |  | Client Construction Engineer |  | Client QMD |  |  | Client O&M/CES
|  |  | Discipline | Lead
Date
Name
Signature
N.J Devani Builders Pvt.Ltd |  |  | ITP No. : NJDBPL-ISBL-ITP-CS:009 |  |  | Inspection and Test Plan For Construction of Building
Rev No. : 06
Date : 22.02.2017
Sheet No. : 04 OF 09
Area :- ISBL Contractor : N.J.Devani Builders Pvt.Ltd.
Building Name / Description - Civil Works For Construction of Sub Station cum Control Building. Work Order No. : 230068628
Sr. | Activity Description |  |  | Controlling Document | Acceptance criteria | Verifying Forms | Contractor | Client
[8 empty] | Construction |  | QMD | O&M/CES
[8 empty] | Disc | Lead
11.2 | Determination of Field Density of the compacted soil/soling sub base preparation & acceptance PCC |  |  | Approved Drawing / Specification & EPCMD-2QM00-JEP-CS-026 | Approved Drawing / Specification & EPCMD-2QM00-JEP-CS-026 | Compection Test Report | H | H | S | S | S
11.3 | Check approved flooring material is used, |  |  | Approved Drawing / Specification | Approved Drawing / Specification | EPCMD 2QM00FMTCS074 | H | H | S | S | S
11.4 | Check for base PCC, slope and level of the floor |  |  | Approved Drawing / Specification | Approved Drawing / Specification | EPCMD 2QM00FMTCS074 | H | H | S | S | S
11.5 | Check proper application & curing |  |  | Approved Drawing / Specification | Approved Drawing / Specification | EPCMD 2QM00FMTCS074 | H | S | S | S | S
12 | Plaster Work
12.1 | Check for suitability of sand, water, cement etc. |  |  | Approved Drawing / Specification | Approved Drawing / Specification | Material Test Report | H | DR | DR | DR | DR
12.2 | Check that sand being used is sieved. |  |  | Approved Drawing / Specification | Approved Drawing / Specification | EPCMD 2QM00FMTCS076 | H | S | S | S | S
12.3 | Check correctness in batching as per mix proportion |  |  | Approved Drawing / Specification & EPCMD-2QMOO-JEP-CS-030 | Approved Drawing / Specification & EPCMD-2QMOO-JEP-CS-030 | EPCMD 2QM00FMTCS076 | H | S | S | S | S
12.4 | Application of Plaster |  |  | Approved Drawing / Specification | Approved Drawing / Specification | EPCMD 2QM00FMTCS076 | H | S | S | S | S
12.5 | Check for curing of plaster surface |  |  | Approved Drawing / Specification | Approved Drawing / Specification | EPCMD 2QM00FMTCS076 | H | S | S | S | S
| Contractor Engineer |  | Client Construction Engineer |  | Client QMD |  |  | Client O&M/CES
|  |  | Discipline | Lead
Date
Name
Signature
N.J Devani Builders Pvt.Ltd |  |  | ITP No. : NJDBPL-ISBL-ITP-CS:009 |  |  | Inspection and Test Plan For Construction of Building
Rev No. : 01
Date : 16.07.2013
Sheet No. : 05 OF 09
Area :- ISBL Contractor : N.J.Devani Builders Pvt.Ltd.
Building Name / Description - Civil Works For Construction of Sub Station cum Control Building. Work Order No. : 230068628
Sr. | Activity Description |  |  | Controlling Document | Acceptance criteria | Verifying Forms | Contractor | Client
[8 empty] | Construction |  | QMD | O&M/CES
[8 empty] | Disc | Lead
13 | Gypsum Plaster - As per Applicable
13.1 | Check Incoming material Verification is as per approved brand |  |  | Approved Drawing / Specification/ Vendor Recommendation | Approved Drawing / Specification/ Vendor Recommendation | Material Test Report | H | H | DR | DR | DR
13.2 | Check the surface preparation and cleanness as per vendor Recommendation. |  |  | Approved Drawing / Specification/ Vendor Recommendation | Approved Drawing / Specification/ Vendor Recommendation | EPCMD 2QM00FMTCS107 | H | H | S | S | S
13.3 | Check and Verify completion of external plaster work before commencement of Gypsum plaster on external wall |  |  | Approved Drawing / Specification/ Vendor Recommendation | Approved Drawing / Specification/ Vendor Recommendation | EPCMD 2QM00FMTCS107 | H | W | S | S | S
13.4 | Application of plaster with measures, correctness and completeness. |  |  | Approved Drawing / Specification/ Vendor Recommendation | Approved Drawing / Specification/ Vendor Recommendation | EPCMD 2QM00FMTCS107 | H | H | S | S | S
| Contractor Engineer |  | Client Construction Engineer |  | Client QMD |  |  | Client O&M/CES
|  |  | Discipline | Lead
Date
Name
Signature
N.J Devani Builders Pvt.Ltd |  |  | ITP No. : NJDBPL-ISBL-ITP-CS:009 |  |  | Inspection and Test Plan For Construction of Building
Rev No. : 06
Date : 22.02.2017
Sheet No. : 06 OF 09
Area :- ISBL Contractor : N.J.Devani Builders Pvt.Ltd.
Building Name / Description - Civil Works For Construction of Sub Station cum Control Building. Work Order No. : 230068628
Sr. | Activity Description |  |  | Controlling Document | Acceptance criteria | Verifying Forms | Contractor | Client
[8 empty] | Construction |  | QMD | O&M/CES
[8 empty] | Disc | Lead
14 | Ready to Use Cement: sand Plaster
14.1 | Check Incoming material Verification is as per approved brand |  |  | Approved Drawing / Specification/ Vendor Recommendation | Approved Drawing / Specification/ Vendor Recommendation | Material Test Report | H | H | DR | DR | DR
14.2 | Check the surface preparation and cleanness as per vendor Recommendation. |  |  | Approved Drawing / Specification/ Vendor Recommendation | Approved Drawing / Specification/ Vendor Recommendation | EPCMD 2QM00FMTCS106 | H | H | S | S | S
14.3 | Application of plaster with measures, correctness and completeness. |  |  | Approved Drawing / Specification/ Vendor Recommendation | Approved Drawing / Specification/ Vendor Recommendation | EPCMD 2QM00FMTCS106 | H | H | S | S | S
14.4 | Check for curing of plaster surface |  |  | Approved Drawing / Specification/ Vendor Recommendation | Approved Drawing / Specification/ Vendor Recommendation | EPCMD 2QM00FMTCS106 | H | S | S | S | S
15 | Plumbing & Sanitary Work
15.1 | Check Piping layout |  |  | Approved Drawing / Specification | Approved Drawing / Specification | EPCMD 2QM00FMTCS077 | H | H | S | S | S
15.2 | Check Piping material and fitting free from damage & as per approved brand |  |  | Approved Drawing / Specification | Approved Drawing / Specification | EPCMD 2QM00FMTCS077 | H | H | S | S | S
| Contractor Engineer |  | Client Construction Engineer |  | Client QMD |  |  | Client O&M/CES
|  |  | Discipline | Lead
Date
Name
Signature
N.J Devani Builders Pvt.Ltd |  |  | ITP No. : NJDBPL-ISBL-ITP-CS:009 |  |  | Inspection and Test Plan For Construction of Building
Rev No. : 06
Date : 22.02.2017
Sheet No. : 07 OF 09
Area :- ISBL Contractor : N.J.Devani Builders Pvt.Ltd.
Building Name / Description - Civil Works For Construction of Sub Station cum Control Building. Work Order No. : 230068628
Sr. | Activity Description |  |  | Controlling Document | Acceptance criteria | Verifying Forms | Contractor | Client
[8 empty] | Construction |  | QMD | O&M/CES
[8 empty] | Disc | Lead
15.3 | Installation and joint of piping |  |  | Approved Drawing & Specification | Visual inspection & Specification | EPCMD 2QM00FMTCS077 | H | W | S | S | S
15.4 | Check continuty and completeness of the piping work, required slope |  |  | Approved Drawing & Specification | Approved Drawing & Specification | EPCMD 2QM00FMTCS077 | H | H | S | S | S
15.5 | Check proper fitting of all fixtures & their functioning |  |  | Approved Drawing & Specification | Visual inspection & Specification | EPCMD 2QM00FMTCS077 | H | W | S | S | S
15.6 | Final testing and checking of system |  |  | Approved Drawing / Specification | Visual inspection & Specification | EPCMD 2QM00FMTCS077 | H | H | S | S | S
16 | Painting
16.1 | Material verification as per approved brand |  |  | Approved Drawing / Specification & Manufacturer Specification | Approved Drawing / Specification & Manufacturer Specification | EPCMD 2QM00FMTCS075 | H | H | S | S | S
16.2 | Surface preparation |  |  | Approved Drawing / Specification & Manufacturer Specification | Approved Drawing / Specification & Manufacturer Specification | EPCMD 2QM00FMTCS075 | H | H | S | S | S
16.3 | Application of suitable primer and curing of primer |  |  | Approved Drawing / Specification & Manufacturer Specification | Approved Drawing / Specification & Manufacturer Specification | EPCMD 2QM00FMTCS075 | H | S | S | S | S
16.4 | Painting application and curing between subsequent coat |  |  | Approved Drawing / Specification & Manufacturer Specification | Approved Drawing / Specification & Manufacturer Specification | EPCMD 2QM00FMTCS075 | H | S | S | S | S
| Contractor Engineer |  | Client Construction Engineer |  | Client QMD |  |  | Client O&M/CES
|  |  | Discipline | Lead
Date
Name
Signature
N.J Devani Builders Pvt.Ltd |  |  | ITP No. : NJDBPL-ISBL-ITP-CS:009 |  |  | Inspection and Test Plan For Construction of Building
Rev No. : 06
Date : 22.02.2017
Sheet No. : 08 OF 09
Area :- ISBL Contractor : N.J.Devani Builders Pvt.Ltd.
Building Name / Description - Civil Works For Construction of Sub Station cum Control Building. Work Order No. : 230068628
Sr. | Activity Description |  |  | Controlling Document | Acceptance criteria | Verifying Forms | Contractor | Client
[8 empty] | Construction |  | QMD | O&M/CES
[8 empty] | Disc | Lead
16.5 | Painting / varnishing / polishing of wooden work |  |  | Approved Drawing / Specification & Manufacturer Specification | Approved Drawing / Specification & Manufacturer Specification | EPCMD 2QM00FMTCS075 | H | S | S | S | S
17 | Fitting of Doors & Windows
17.1 | Fitting of Doors & Windows |  |  | Approved Drawing & Specification | Approved Drawing & Specification | EPCMD 2QM00FMTCS015 | H | S | S | S | S
17.2 | Completion of glazing work as applicable |  |  | Approved Drawing / Specification | Approved Drawing / Specification | Vendor specified Checklist | H | S | S | S | S
18 | Waterproofing & Testing
18.1 | Waterproofing work for plinth wall, sunk portion in toilet block, terrace etc as applicable. |  |  | Approved Drawing / Specification | Approved Drawing / Specification | EPCMD 2QM00FMTCS042 EPCMD 2QM00FMTCS020 | H | H | S | S | S
18.2 |  | Water proofing of Roof Slab with APP membrane Application and over deck insulation |  | Approved Drawing / Specification | Approved Drawing / Specification | EPCMD 2QM00FMTCS111 | H | H | S | S | S
18.3 | Leak test of roof slab |  |  | Approved Drawing / Specification | Approved Drawing / Specification | EPCMD 2QM00FMTCS111 | H | H | H | S | H (CES)
| Contractor Engineer |  | Client Construction Engineer |  | Client QMD |  |  | Client O&M/CES
|  |  | Discipline | Lead
Date
Name
Signature
N.J Devani Builders Pvt.Ltd |  |  | ITP No. : NJDBPL-ISBL-ITP-CS:009 |  |  | Inspection and Test Plan For Construction of Building
Rev No. : 06
Date : 22.02.2017
Sheet No. : 09 OF 09
Area :- ISBL Contractor : N.J.Devani Builders Pvt.Ltd.
Building Name / Description - Civil Works For Construction of Sub Station cum Control Building. Work Order No. : 230068628
Sr. | Activity Description |  |  | Controlling Document | Acceptance criteria | Verifying Forms | Contractor | Client
[8 empty] | Construction |  | QMD | O&M/CES
[8 empty] | Disc | Lead
18.4 | Leak test of other structure (i.e Tanks) |  |  | Approved Drawing / Specificaton | Approved Drawing / Specificaton | EPCMD 2QM00FMTCS096 | H | H | H | S | H (CES)
19 | Release of completed Building |  |  | Approved ITP / Drawing / Specificaton | Completeness of work as per approved drawing | Building Release note | H | H | DR | DR | DR
| Contractor Engineer |  | Client Construction Engineer |  | Client QMD |  |  | Client O&M/CES
|  |  | Discipline | Lead
Date
Name
Signature

## ITP FOR PLUMBING
Inspection Report For Plumbing Work
Report No. : |  |  |  | Date :
Structure Description : Drawing No. : Rev.
Unit / Bldg. : Structure:
Sr.No. | Item Description |  |  |  |  | Observation
[6 empty] | N.J.Devani | Client
1 | Check that all material like pipes, fittings, valves,cocks etc are from approved brand as given in specification / drawings.
2 | Check that all pipes, fittings are under good condition, cleaned and not damaged on visual inspection
3 | Check that grooves of required size for concealing of pipes is made as per drawing requirement
4 | Check that plumbing lay out is checked and verified as per drawing
5 | Check that position of all Traps, Cock, Valves etc is as per drawings
6 | Check for proper fixing with wall of all exposed pipe
7 | Check that required slope in all drainage piping is maitained as per drawing
8 | Check proper sealing of all joints of piping and fitting
9 | Check that all grooves, holes, surface chipping made for pipe laying and fixing of the fittings are repaired properly
10 | Check the entire system of piping including fitting is tested for it's completeness, effectiveness and required pressure as per drawing/specification.
|  | N.J.Devani Builders Pvt.Ltd. | Client Construction Engineer |  | Client O&M/TPI
Signature
Name
Date
Format No. EPCMD-2QMOOFMTCS077, Rev.00 Date 01.09.2013
Page 1 of 1

## PLUMBING PRESURE
PLUMBING INSTALLATION INSPECTION RECORD
Report No. : | [5 empty] | Date :
Structure Description : |  | Drawing No:- |  |  | Rev.
Unit / Bldg No. : |  |  |  | Area :-
Sr.No. | DESCRIPTION | PRESSURE | TIME |  | OBSERVATION | DATE | REMARK
|  |  | START | END
1 | Hydro Testing of water supply (CPVC ) piping
2
3
4
5
6
7
8
9
10
| N.J.DEVANI BUILDERS PVT.LTD | RIL (QMD) |  | Q & M / TPI |  | RIL CLIENT
SIGN
NAME
DATE
Format No. EPCMD-001 Rev.0 Date 08.07.2016
Page 1 of 1

## ITP FLOORING
Inspection Report For Flooring
Report No. : |  |  |  | Date :
Area : Drawing No. : Rev.
Unit No.. :
Sr.No. | [5 empty] | Status
[6 empty] | N.J.Devani | Client
1 | Preparation of Base :
1.1 | Ensure that underlying soil is properly compacted as per specification and compaction tests carried out.
1.2 | Check and ensure application of anti termite treatment, and laying of conceal services (As application)
1.3 | Check that base concrete preparation is complete in all respects eg. Completion of curing period, top surface, slope, roughening activity & coating with cement slurry as per spec.
2 | Tile, Marble & Kota Stone Flooring :
2.1 | Verify Type & dimension, colour & shade of the tiles/slabs as per relevant drawing/spec.
2.2 | Check the wearing layer of tiles is free from any projections, depressions, cracks, holes, cavities and other blemishes.
2.3 | Check for Mix proportion, thickness & level & slope of bedding mortar as per relevant drawing/spec.
2.4 | Ensure laying of tiles as per required pattern with sealing of the joints with applicable material and movement is restricted till setting of base mortar.
2.5 | Verify the junction between tile work and wall plaster/skirting/dado and pointing/finishing work is as per relevant drawing/spec.
|  | N.J.Devani Builders Pvt.Ltd. | Client Construction Engineer |  | Client O&M/TPI
Signature
Name
Date
Format No. EPCMD-2QMOOFMTCS074, Rev.00 Date 01.09.2013
N.J.DEVANI BUILDERS PVT.LTD. |  |  |  | Inspection Report For Flooring
Report No. : |  |  |  | Date :
Area : Drawing No. : Rev.
Unit No.. :
Sr.No. | Description of the Activities |  |  |  |  | Status
[6 empty] | N.J.Devani | Client
2.6 | Ensure curing, polishing & finishing as per specification.
3 | Granolithic Floor Topping : (Cement Concrete Flooring)
3.1
3.2
3.3
3.4
3.5
|  | N.J.Devani Builders Pvt.Ltd. | Client Construction Engineer |  | Client O&M/TPI
Signature
Name
Date
Format No. EPCMD-2QMOOFMTCS074, Rev.00 Date 01.09.2013
Page 2 of 4

## Concrete Placement
Concrete Placement, Finishing & Curing Inspection
Report No. : |  |  |  |  | Date :
Reference No. & Description of Structures :
Date of Cast : Time concrete start: Time concrete Finish:
Activities / Items to be Checked |  |  |  | Status | Activities / Items to be Checked | [8 empty] | Status
1 | Final Wash Down & Clean out of Forms / Rebar satisfactory. All accumulated water is removed |  |  |  | 9 | Reinforcement / Water bar / Embedded Items/bolts & pockets/templates/supports etc are undistrubed during placement.
2 | Construction joints Coated with Bonding Agent (If required) |  |  |  | 10 | Check & verify correct pouring sequence to avoid formation of cold joint
3 | All Concrete, Placed within 60 Minutes of Batching |  |  |  | 11 | Leveling complete with required finished surface
4 | Check Concrete Consistency, Slump and Workability Satisfactory |  |  |  | 12 | Check installation of polythene covering during rainy and very hot weather.
5 | *Free Fall Drops Less than 1.50m for normal mix using chute, bucket. Etc. & 2.40m for pump mix. |  |  |  | 13 | Covering with wet Hessian cloth/ponding/application of curing compound
6 | Distribution Across Pour Area Satisfactory |  |  |  | 14 | Check Form Striking date - & support removal Date -
7 | Concrete Layer thickness Properly Regulated (150mm First Layer, 400mm Max Thereafter) Ensure that panel wise casting as planned is carried out in case of paving |  |  |  | 15 | Check Wet Curing | 1 | 2 | 3 | 4 | 5 | 6 | 7
[5 empty] | 16 | Check all concrete for visible Surface Defects, If defects are found repair properly. Reference repair Record No. NJDBPL 2QMOOFMTCS043.
8 | Vibration / Compaction Satisfactory |  |  |  | 17 | Check for proper application of protective coating as per specification requirement as applicable.
Comments / Discrepancies :
*Free fall shall be reduced if mix is segregating
|  | N.J.Devani Builders Pvt.Ltd. | Client Construction Engineer |  |  |  | 3: Client O&M/TPI
Signature
Name
Date
Format No. EPCMD-2QMOOFMTCS008, Rev.01 Date 01.09.2013
Page 1 of 1

## False Ceiling
CHECK LIST FOR FALSE CEILING
DATE: |  |  |  | UNIT/BUILDING NO:
STRUCTURE DESCRIPTION: |  |  |  | FLOOR LEVEL:
TYPE OF FALSE CEILING : |  |  |  | DRG. NO. & REV NO.:
SR NO | ACTIVITY DESCRIPTION |  |  |  |  | STATUS
PRECHECK | [5 empty] | N.J.DEVANI | RIL
1 | Check for approved False Ceiling material
2 | Check for frame sections,fixtures etc. approval as per drawing and specification
3 | Check for material is in good condition and stacked properly at site
4 | Check & verify of level marking line of ceiling in wall from FFL
PROCESS CHECK
5 | Check for fixing of frames with screws with proper level and verticality as per drawing and specification.
6 | Check the spacing of framework as per drawing and specification.
7 | Check provision like trap doors, light fixtures and other fixtures.
POST CHECK
8 | Check for line, level, verticality of False Ceiling.
9 | Check for ceiling board damages like scratches,breakage,paint/mortar dropping etc.
COMMENTS:
|  | Contractor Engg. | Reliance Construction Engg. |  | Reliance O & M/ TPI
Signature
Name
Date
Format no.:EPCMD2QMOOFMTCS003,Rev 00 Date: 03.03.2016

## False Flooring
CHECK LIST FOR FALSE FLOORING
DATE: |  |  |  | UNIT/BUILDING NO:
STRUCTURE DESCRIPTION: |  |  |  | FLOOR LEVEL:
DRG. NO. & REV NO.:
SR NO | ACTIVITY DESCRIPTION |  |  |  |  | STATUS
PRECHECK | [5 empty] | N.J.DEVANI | RIL
1 | Check for approved false floor material
2 | Check for support sections,fixtures etc. approval as per drawing and specification
3 | Check for material is in good condition and stacked properly at site
4 | Check that slab/grade slab level as drawing and specification.
5 | Check & verify of level marking line of floor in wall from FFL
PROCESS CHECK
6 | Check for fixing of supports with fastner/screws with proper level and verticality as per drawing and specification.
7 | Check the spacing of supports as per drawing and specification.
8 | Check provision like elect.panels and other fixtures.
POST CHECK
9 | Check for line, level of false flooring.
10 | Check for floor board damages like scratches,breakage,dropping etc.
COMMENTS:
|  | Contractor Engg. | Reliance Construction Engg. |  | Reliance O & M/ TPI
Signature
Name
Date
Format no.:EPCMD2QMOOFMTCS004,Rev 00 Date: 03.03.2016

## Door & Window
CHECK LIST FOR DOOR AND WINDOW
DATE: |  |  |  | UNIT/BUILDING NO:
STRUCTURE DESCRIPTION: |  |  |  | FLOOR LEVEL:
TYPE OF DOOR AND WINDOW: |  |  |  | DRG. NO. & REV NO.:
SR NO | ACTIVITY DESCRIPTION |  |  |  |  | STATUS
PRECHECK | [5 empty] | CONTR. | RIL
1 | Check for approved Door/Window Material
2 | Check for opening sizes,diagonals and finishing meet the requirements
3 | Check for levels & verticality for sills and jambs.
4 | Check for door/window & frame sections,beadings,fixtures etc. approval as per drawing and specification
PROCESS CHECK
5 | Check for fixing of door/window frames and shutters with fasteners/screws with proper level and verticality as per drawing and specification.
6 | Check provision like glasses with rubber gasket, silica sealant fixing,locks,handels and other fixtures.
POST CHECK
7 | Check for line, level, verticality,of frames,doors and windows.
8 | Check for doors/windows protected from damages like scratches,breakage,paint/mortar dropping etc.
9 | Check for proper functioning ofdoors/windows with neat finish.
COMMENTS:
|  | Contractor Engg. | Reliance Construction Engg. |  | Reliance O & M/ TPI
Signature
Name
Date
Format no.:EPCMD 2QMOOFMTCS001,Rev 00 Date: 03.03.2016

## ATT
ANTI-TERMITE TREATMENT
Report No. : |  |  |  | Date :
Anti termite treatment
Unit No.
Grid Location or description of area :
Activities / Items to be Inspected | [5 empty] | Status
1 | Check proposed fill material has been tested and found complying specification requirement (Ref Lab testing report)
2 | Check Drawing No. and revision is current
Drwg No. - Rev.
3 | Check ground level & conditions firm as specified.
4 | Check field compaction test where applicable was conducted and recorded . (Ref. compaction record format no. NJDBPL-2-QM00-FMT-CS-007).
5 | Check that Anti-termite Treatment carried out as per Reliance approval procedure.
6 | Mix 1.0 Litre of Piramid(Chlorpyriphos 20% EC) with19 litres of water to get a 1.0% ai Piramid Emulsion and apply of the below stages.
7 | Stage:1Check that Plinth filling holes up to 500 mm deep and 150 mm centers shall be made along the all beams and columns. The chemical Emulsion shall be poured/sprayed @7.5Ltr/Sqmts of the vertical surface in to these holes.
8 | Stage:2Check that the top surface of consolidated earth in plinth area new soil level below ground floor slab shall be treated with chemical emulsion @ 5.0 Ltr/Sqmts.( diluted liquid)
9 | Check Anti-termite Treatment to structures, if applicable is carried out as per specification/vendor's approved procedure and testing is complete
Comments / Description :-
|  | N.J.Devani Builders Pvt.Ltd. | Reliance Construction Engineer |  | Reliance O&M/TPI
Signature
Name
Date
Format No. EPCMD-2QMOOFMTCS087, Rev.0 Date 21.01.2014

## CUBE TESTING
Format For Concrete Cube Testing Request
Contractor's Name : | [7 empty] | Reliance HOD :
Date of Cube Submission : | [7 empty] | Location / Phone No. :
Sr.No. | Contractor's Name | Date of Casting | Mix Details | Area / Unit No | Main Structure | Structure Detail | Nos of Cube |  | Testing Required |  |  | CMTL Receipt
[9 empty] | 3 Days | 7 Days | 28 Days
|  |  | Contractor's representative |  |  | Reliance execution |  |  |  | Sample received by (CMTL)
Signature
Name
Date
Format No. EPCMD-2QMOOFMT-CS-086, Rev.00 Date 02.07.2011

## ITP PLASTER
Inspection Report For Plaster Work
Report No. : |  |  |  | Date :
Structure Description : Drawing No. : Rev. Bottom Lvl. : |  |  |  |  | Area :
Type of Plaster : Wall thickness : Top Lvl. : |  |  |  |  | Unit / Bldg No. :
Sr.No. | Activities / Items to be Checked | [5 empty] | Status
[7 empty] | N.J.Devani | Client
1 | Check and ensure that bricks/blocks, water, sand, cement brought to site are complying specification requirement, necessary testing is carried out at CMTL (Cnetral Civil Material testing Laboratory) and test results are available.
2 | Check available of 0.035 cum gauge box and suitable size water measures and sieve for seiving for sieving of sand are available at site for mortar preparation.
3 | Check that the surface to be plastered is cleaned of all dust, loose mortar droppings, efflorescence and other foreign matter. Ensure pre-wetting of the surface prior to application of plaster.
4 | Check that all masonary joints are racked, and hacking is made on concrete surface to be plaster
5 | Ensure fixing of 150mm wide expanded GI metal lath of size 25x50mm is fixed on the junction of RCC and masonary work.
6 | Check correctness in the material batching as per specified mix propotion and ensure that only mortar that can be consumed within 30 minutes of mixing prepared at a time.
7 | Check that first coat is of 12mm thk. Followed by finished coat of 8mm in case of sand faced plaster. Ensure that the finished coat is applicable after under coat is set, but not dried and within 48 hours.
8 | Ensure uniform and leveled application of surface with all corners, edges, angles are truly vertical and horizontal as the case be and finished properly.
9 | Check that 6mm length Recron 3S fibes are mixed in the mortar @ 125gms per 50 kg. cement bag. (If specified)
10 | Check that plaster on the top copping of parapet wall is tilting inside for proper drainage of water.
11 | Final external surface of plaster is finished of true with trowel smooth finished or sponged finished rough texture as per requirement. All corners, edges and angles of pillars, parapet etc are truly vertical / horizontal.
12 | Check for minimum 10 days curing is done for all plaster work.
|  | N.J.Devani Builders Pvt.Ltd. | Reliance Construction Engineer |  |  | Reliance O&M/TPI
Signature
Name
Date
Format No. EPCMD-2QMOOFMTCS076, Rev.01 Date 01.09.2013
Page 1 of 1

## ITP PAINTING
Inspection Report For Painting Work
Report No. : |  |  |  | Date :
Structure Description : Drawing No. : Rev.
Type of Painting : Unit / Bldg. : Structure:
Sr.No. | Item Description |  |  |  |  | Observation
[6 empty] | N.J.Devani | Client
1 | Check paint, primer and necessary thinner material is from approved brand and as per drawing/specification requirement
2 | Check that all repair works, plumbing work, elect. Fixture & fittings closing of scaffold opening etc is completed prior to start up of painting work.
3 | Check that surface to be painted is thoroughly cleaned of all dirt, dust, loose mortar dropping, and any other foreign material. Efflorescenece if any shall be cleaned off.
4 | Check that all fine cracks are sealed with POP/Putty/cracks sealant as specified by vendor prior to applying prime coat.
5 | Check application of specified primer and ensure addition of water/thinner as recommended by manufacturer.
6 | Check that paint is applied as per approved colour shceme, and numbers of coats are as specified in drawings, manufacturer's recommendation.
7 | Check uniform application of paint in each coat, free from patches, brush marking etc. Ensure drying between two subsequent coats as per manufacturer's recommendation.
8 | Check and ensure minimum two days water curing to finished coat in case cement base paint is applied.
9 | Check application painting /varnishing/polishing of wood work as applicable and according to manufacturer's recommendation
10 | Check DFT of each coat as per manufacturer's recommendation as applicable in case of painting on metallic surface.
11 | Checked that final finished surface of painting is even and uniform, and without patches, brush marks drops etc.
|  | N.J.Devani Builders Pvt.Ltd. | Reliance Construction Engineer |  | Reliance O&M/TPI
Signature
Name
Date
Format No. EPCMD-2QMOOFMTCS075, Rev.00 Date 01.09.2013
Page 1 of 1

## ITP MASONARY
Inspection Report For Brick / Block Masonary Work
Report No. : |  |  |  | Date :
Structure Description : Drawing No. : Rev. Bottom Lvl. : |  |  |  |  | Area :
Type of Masonary : Wall thickness : Top Lvl. : |  |  |  |  | Unit / Bldg No. :
Sr.No. | Activities / Items to be Checked | [5 empty] | Status
[7 empty] | N.J.Devani | Client
1 | Check and ensure that bricks/blocks, water, sand, cement brought to site are complying specification requirement, necessary testing is carried out at CMTL (Cnetral Civil Material testing Laboratory) and test results are available.
2 | Check availability of 0.035 cum gauge box and suitable size water measures and mechanical mixer are available at site for mortar preparation.
3 | Check correctness of material batching as specified and ensure that only the quantity of mortar which can be consumed within 30 minutes of its mixing is prepared at a time.
4 | Ensure that bricks are soaked & under SSD condition while it is taken for use. Half or cut bricks shall not be used
5 | Check that bricks laying is in English bond pattern with frog up, built up in uniform layer and no portion is raised more than one meter above the general construction level.
6 | Check that brick work is not carried out more than 1200mm in a day, necessary pipe sleeves, weep holes, opening etc as per drawing requirement are provided with correct diminsion.
7 | Check that all vertical joints are staggered and joint thickness is 10 to 12mm. Ensure that joints are racked to depth of 10mm
8 | Check for proper reinforcement as per specification requirement for half brickwork
9 | Check for verticality and alignment of the brickwork. Deviation shall not be more than tolerance limt i.e.10mm in alignment and 5mm in verticality for 3m ht.
10 | Check for minimum 7 days curing of all masonary work
|  | N.J.Devani Builders Pvt.Ltd. | Reliance Construction Engineer |  |  | Reliance O&M/TPI
Signature
Name
Date
Format No.EPCMD-2QMOOFMTCS059, Rev.01 Date 01.09.2013
Page 1 of 1

## ITP REPAIR
Repair Record For Concrete Cracks, Honey comb
Report No. : |  |  |  |  | Date :
Reference No. or Description of Structure :
Unit No. :
Activities / Items to be Inspected
1 | Identify and demark defective portion of concrete
2 | Check sketch, drawing or method statement for repair is approved and available at site. (attach copy)
3 | Check approval to cut rebar. (If applicable)
Area Released For Cutting, Chipping, Or Crack Repair
N.J.Devani Engineer |  |  |  | Client Engineer
Activities / Items to be Inspected
4 | Check that all loose material is removed and defected portion is properly opened up for repair material (If applicable)
5 | Replacement / treatment of existing bars as applicable
6 | Pressure grouting if required is carried out with specified material and with approved method
7 | Check bonding agent applied (If necessary)
8 | Install necessary form work with required window of material placing as to suit site condition and types of material used for repair.
9 | Check proper repair materials, polymer modified morrat/1:3 cement : Fine Sand mortar, or any other specifed in per approved procedure is used.
10 | Check materials properly applied as per namuf. Recommendation's / approved procedure
11 | Check curing application (If required)
Comments / Discrepancies :
Concrete Repairs Complete Have Been Completed Satisfactorily
|  | N.J.Devani Builders Pvt.Ltd. | Reliance Construction Engineer |  |  | Reliance O&M/TPI
Signature
Name
Date
Format No. EPCMD-2QMOOFMTCS043, Rev.00 Date 01.11.2010
Page 1 of 1

## WATERPROOF MEMBRANE
Application Record for Water Proof Membrane
Report No. : |  |  |  | Date :
Reference No. or Description of structure :
Membrane Type & Manufacturer :
Activity / Items to be checked | [5 empty] | Status
1 | Check concrete blinding is satisfactory, check surface is smooth & free of sharp protrusions & Honeycomb.
2 | Check minimum cured age of concrete compliant with Manufacturers Recommendations.
3 | Check Interior corners mitered 45' & Exterior corners are chamfered
4 | Check concrete surface is clean, dry & free of all dirt, oil, grease & dust.
Concrete Surface Inspected & Ready for Membrane Application
5 | Check and verify that all material e.g. primer, membrane etc are of approved brand and test certificates are available at site.
6 | Check Primer applied as per Manufacturer's Recommendations.
7 | Check interior & exterior corners fitted with 300mm wide strips of membrane materials.
8 | Check membrane applied as per Manufacturer's Recommendations
9 | Check that side laps are as per Manufacturer's Recommendations (150mm Min.)
10 | Check that all air bubbles removed.
11 | Check that foot traffic is prohibited and signs are placed at appropriate places, if required.
12 | Check waterproof collars placed around all penetrations
Membrane Application Complete & Ready For Screed or Protection Board
13 | Check protection board fitted to vertical surfaces prior to backfill. (if required)
(All above requirements are generic, job specific formats shall be developed as per Vendor's recommendation.)
Comments / Descrepancies :
|  | N.J.Devani Builders Pvt.Ltd. | Reliance Construction Engineer |  | Reliance O&M/TPI
Signature
Name
Date
Format No. EPCMD-2QMOOFMTCS042, Rev.00 Date 05.12.2012
Page 1 of 1

## WATER PROOFING
Inspection of Waterproof Coating
Report No. : |  |  |  | Date :
Description of Structures to be waterproofed :
Bldg No. / Name / Plant :
Contractor : N. J. Devani Builders Pvt. Ltd.
Waterproofing Type & Manufufacturer :
1.0 Inspection Activity (Surface Preparation) | [5 empty] | Status
[6 empty] | Contractor | Client
1.1 | Check concrete surface preparation complete & satisfactory for water proofing as per specification and vendor's recommendation.
1.2 | Check concrete surface clean and dry, free form oil, grease, hessian fibre, dust and any other foreign material.
1.3 | Check screed concrete, if required, is carried out as per slope, thickness and grade mentioned in drawing.
1.4 | Check that all visible cracks in concrete surface are filled up properly with approved procedure.
1.5 | Check that size of triangle fillet at junction of horizontal and vertical face is as per drawing. (If applicable)
2.0 Inspection Activity (Liquid Coating System)
2.1 | Check that weather condition is suitable as per vendor's recommendation (RH, Dew Point, temperature etc).
2.2 | Check that approved brand of material with manufacturer's test certificate is available at site.
2.3 | Check mixing & application of Prime coat as per Manufacturer's recommendations.
Date : Wet film thickness :
Dry film thickness :
2.4 | Check mixing & application of First coat as per Manufacturer's recommendations.
Date : Wet film thickness :
Dry film thickness :
2.5 | Check mixing & application of Second coat as per Manufacturer's recommendations.
Date : Wet film thickness :
Dry film thickness :
2.6 | Check curing time between subsequent coats satisfactory.
2.7 | Check Polythene sheet is folded up flush with foundation all around 150 mm minimum. (If applicable)
2.8 | Verify splash zone epoxy coating, completeness and conformance, wherever applicable.
2.9 | Check all flexible protection boards are installed. Treatment at joints is carried out as per vendor recommendation.
2.1 | Check compliance of leakage test as per specification and drawing requirement.
3.0 Inspection Activity (Membrane Base Treatment)
3.1 | Check that approved brand of material with manufacturer's test certificate is available at site.
3.2 | Check that approved brand of cold bituminous primer is applied at the rate of 0.3 litre/sqm
3.3 | Check that all outlets are treated and are fixed as per drawing requirement.
3.4 | Check that polymer modified membrane is an approved type, with or without mineral finish, as per drawing/specification requirement is applied as per vendor recommendation.
3.5 | Check for overlap of membrane, minimum 75mm on length, 100mm on width, and membrane is properly thermo fused.
3.6 | Check for proper termination of the membrane as per drawing requirement, and joints at termination are sealed properly.
3.7 | Check for compliance of leakage test with 75mm water head for minimum 48 hours.
(All above requirements are generic, job specific formats shall be developed as per Vendor's recommendation.)
Comments / Descrepancies :
|  | N.J.Devani Builders Pvt.Ltd. | Client Construction Engineer |  | Client O&M/TPI
Signature
Name
Date
Format No. EPCMD-2QMOOFMTCS020, Rev.01 Date 05.12.2012

## POUR CARD
Concrete Pour Card
Report No. : |  |  |  |  | Date :
Concrete Grade : |  |  | Date Required : |  | Time Required : |  | Quantity Required :
Reference No, Type & Description of Structure (s) :
Area / Location :
Activities / Items to be Checked | [7 empty] | Status
1 | Rebar, Form & Embedded Items Ready For Casting (Ref formats NJDBPL - 2QMOOFMTCS011 & 14 as apllicable)
2 | Check Forms are clean and free of all tiewires, nails, chips of timber debris etc.
3 | Check availability of concrete pour plan & proper deployment of concrete pouring equipments, proper access to pouring place.
4 | Check concrete batch order information is complete & correct, including quantity, mix design, temperature etc.
Comments / Discrepancies :
Concrete structure is ready for the pour
|  | N.J.Devani Builders Pvt.Ltd. |  | Reliance Construction Engineer |  |  | Reliance O&M/TPI
|  |  |  | Discipline Engineer |  | Lead
Signature
Name
Date
Format No. EPCMD-2QMOOFMTCS015, Rev.02 Date 16.07.2013
Page 1 of 1

## PRE-POUR STRUCTURE
Pre-Pour Inspections For Concrete structure
Report No. : |  |  |  | Date :
Reference Number of Structure :
Description of the Structure :
Sr.No | Activities to be checked |  |  |  |  | Status after check
1 | Record Construction drawing & check and ensure for its latest revision number.
Drg No. - Rev. No. -
2 | Check existing concrete surface is properly scabbled/applied bonding agent as per requirement
3 | Check reinforcement bar are free from rust, scale, grease or any other foreign material
4 | Verify that rebar meets project specification requirement and of specified grade.
5 | Check rebar size, quality & spacing conforms with drawings
6 | Check correctness of lap splice for length, location & staggering as per drawing/spec. |  |  |  |  | Lap Length :
Diameter :
Location :
7 | Ensure proper fitting & alignment of mechanical threaded couplers/Groutec couplers as applicable and fixed as per type of couplers
Numbers of couplers : ……………………………………
Position/Types : …………………………………..
8 | Check placement tolerance : Bar spacing + 15mm, Cover + 10mm/-0, Tie & stirrups spacing + 15mm |  |  |  |  | Spacing :
Cover :
9 | Check spacers and chairs for correct size and properly distributed |  |  |  |  | Nos :
10 | Check bars are adequately tied & chairs securely fastened.
11 | Check the cover block, properly distributed to give uniform cover as per drawings.
12 | Check correct position, alignment, dimension and securement of water bar as correct as specified in drawing. |  |  |  |  | Type of water bar :
13 | Check all insert plate are painted, fixed and secured properly as per drawing requirement,
Types of IP : ………………………………………….
Reinforcement work completed and structure is released for erection of formwork
14 | Check correctness of formwork in terms of surface condition, free from perforation, cracks, pinholes and any other foreign material.
15 | Check form work dimension as per drawing requirement & alignment, Fitting of tie roads, verticality and plum are correct.
|  | N.J.Devani Builders Pvt.Ltd. | Reliance Construction |  | Reliance O&M/TPI
|  |  | Discipline Engineer | Lead
Signature
Name
Date
Format No. EPCMD-2QMOOFMTCS014, Rev.03 Date 02.10.2013
Page 1 of 2
Pre-Pour Inspections For Concrete structure
Report No. : |  |  |  | Date :
Reference Number of Structure :
Description of the Structure :
Sr.No | Activities to be checked |  |  |  |  | Status after check
16 | Check release agent applied to formwork (Prior to fixing rebar)
17 | Check supporting & staging to form work as per pre planned/approved requirement.
18 | Check position, dimension of expansion & contraction joint (If applicable)
19 | Check anchor bolts & Template are secured properly in position & level are correct as per drawing requirement (Verify with survey)
20 | Check all civil piping fixed & ready for casting and is conformant with drawings.
21 | Check all embedded electrical items, inserts, other mechanical items fixed & ready for casting and is conformant with drawings.
22 | Check and verify position, size of lifting lugs, grouting pipe etc (precast element)
23 | All setting out verified by surveyor and all dimension checked and within tolerance. (Attached surveyors report)
|  | N.J.Devani Builders Pvt.Ltd. | Reliance Construction |  | Reliance O&M/TPI
|  |  | Discipline Engineer | Lead
Signature
Name
Date
Format No. EPCMD-2QMOOFMTCS014, Rev.03 Date 02.10.2013
|  | N.J.Devani Builders Pvt.Ltd. | Reliance Construction |  | Reliance O&M/TPI
|  |  | Discipline Engineer | Lead
Signature
Name
Date
Format No. NJDBPL-2QMOOFMTCS014, Rev.03 Date 02.10.2013
Page 2 of 2

## PRE-POUR PAVING
Pre Pour Inspection Record - Concrete paving work
Report No. : |  |  |  |  | Date :
Reference No. & Description of Structures :
Activities / Items to be Checked |  |  |  | Status | Activities / Items to be Checked |  |  | Status
1 | Record Const. Drawing & check revision is current Drwg. No. Rev. |  |  |  | 9 | Check release agent applied to formwork. (prior to fixing rebar)
2 | Check proper placement of polythene sheet with minimum 150mm overlap. |  |  |  | 10 | Check position and reinforcement of all pipe supports as per drawing requirement.
3 | Check that rebar are free from rust, scale, grease oil etc. and placed with spacing as per drawing. |  |  |  | 11 | Check all underground drainage installed & in place ready for casting.
4 | Check reinforcement lap length as per drawing and laps are straggered. Check proper fixing & alignment of couplers if used. |  |  |  | 12 | Check all embedded civil, electrical, mechanical items are installed properly, in place and ready for casting.
5 | Check reinforcement placement tolerances : Bar spacing +/- 15mm maximum Cover =10mm/-0, Tie & stirrups spacing +/- 15mm |  |  |  | 13 | Check that dimension & location of expansion and contraction joint as per drawing requirement.
6 | Check that shuttering is clean, even and of good quality. |  |  |  | 14 | Check that filler boards are fixed to all junctions of paving & foundation.
7 | Check proper placement of all concrete cover blocks, Spacer/chairs etc. |  |  |  | 15 | Check proper placing dowel bars with cap for expansions joints.
8 | Check formwork placement, alignment and supports. |  |  |  | 16 | All setting out verified by surveyor and all dimensions checked and correct to within tolerance. (Attach surveyors report)
Rebar, Formwork & Embedded Items Inspected And Ready for Casting.
|  | N.J.Devani Builders Pvt.Ltd. | Reliance Construction Engineer |  |  |  | Reliance O&M/TPI
Signature
Name
Date
Format No. EPCMD-2QMOOFMTCS011, Rev.01 Date 14.12.2012
Page 1 of 1

## CONCRETE RECIEVEL
Concrete Receival Inspection
Report No. : | [6 empty] | Date :
Unit No. :
Reference No & Description of Structure (s) :
Contractor :
Pour Card Serial No. : |  |  |  | Time Limit : (** 60 minutes max between mixing and placing of concrete.) |  | Concrete maximum temperature Limit : 30' C. (Typical ) Max. 35' C |  |  | Slump : Shall be such that concrete can be placed, transported and compacted without segregation. Actual value to be measured.
Batch Plant No. :
Con Vol. Cubic Metres :
Mix Designation :
Truck No. | Ticket No. | Check Design Mix | Batch Time | Time Arrived | Time of Discharge Start | Time of Discharge Finish | Discharge Quantity M3 | Concrete Temp. 'C in position | Ambient Air Temp 'C | Concrete Slump mm | Cube* Ident. No.
*Separate record of cube test results shall be maintained.
** One time second dosage of admixture may be added at site as per design mix, if concrete pouring is delayed.
Comments :
|  | N.J.Devani Builders Pvt.Ltd. |  |  | Reliance Construction Engineer |  |  |  | Reliance O&M/TPI
Signature
Name
Date
Format No. EPCMD-2QMOOFMTCS010, Rev.01 Date 27.10.2012
Page 1 of 1

## SOIL COMPACTION
SOIL COMPACTION TEST REPORT
Contractor :- N.J.Devani builders Pvt.Ltd.
DLBD Of sand :- Kg / Cum
Wt. of sand in cone :- Kgs
MDD of soil determined at laboratory : kg / cum (OMC = %)
Lacation :
Cone calibration status : Yes / No
Layer:
Date :
Sr. No | Description |  |  | S - 1 | S - 2 | S - 3
1 | Wt. of sand in pouring cylinder before pouring (kgs)
2 | Wt. of sand in pouring cylinder after pouring (kgs)
3 | Wt. 0f sand in poured into the hole + cone (kgs)=(C1-C2)
4 | Wt. 0f sand in poured into the hole (kgs)=(C3-0.366)
5 | Wt.of soil extracted from the hole (kgs)
6 | Vol. of sand poured into the hole ( cum )= ( C4/1386)
7 | Wet density of soil in Kg / cum = (C5/C6)
8 | Moisture of soil in %
9 | Dry density of soil in Kg / Cum = (C7X100)/(100+C8)
10 | Degree of compaction in % with ref.to MDD =C9X100/2040
11 | Remark
|  | N.J.DEVANI BUILDERS PVT. LTD. | RELIANCE CONSTRUCTION ENGINEER.
Signature:-
Name:-
Date:-
Format No. EPCMD-2QMOOFMTCS007, Rev.01 Date 01.11.2012

## BLINDING
Concrete Blinding Inspection Record
Report No. : | [5 empty] | Date :
Complete Reference Number for the Foundation. :
Unit NO. : ………………………………………. , Area : ………………………………………
Inspection Activity | [6 empty] | Status
1 | Verify that excavation and base confirmation checks on Form NJDBPL-2QM00FMTCS003 have been carried out and completed prior to start of job.
2 | Latest Construction Drawing and Revision
Drwg No. - Rev.
3 | Placement of Polythene sheeting/Antitermit treatment is carried out as per drawing requirement (If applicable)
4 | Pit size checked and blinding dimension marked & level demarcation is carried out.
5 | Check Placement arrangement for blinding concrete without segregation
6 | Check blinding concrete Class and Designation is correct
7 | Check placing complete within 60 minutes of concrete mixing time.
8 | Check quality of fresh blinding visually satisfactory
9 | Check concrete placing without segregation, conformant and satisfactory and as per required level.
10 | Check proper placement and compaction of concrete
11 | Ensure that blinding top is as per drawing requirement. | [5 empty] | Blinding concrete top Level………………………..
12 | Wet curing sarisfactory |  | In days | 1st | 2nd | 3rd
|  |  | 4th | 5th | 6th | 7th
Comments :
Blinding Placement & Curing Complete & Conformant
|  | N.J.Devani Builders Pvt.Ltd. |  | Reliance Construction Engineer |  |  | Reliance O&M/TPI
Signature
Name
Date
Format No. EPCMD-2QMOOFMTCS005, Rev.01 Date 01.12.2012
Page 1 of 1

## BACKFILLING
Earthwork Backfilling - Foundation & Pavement
Report No. : |  |  |  | Date :
Earthworks Pre-Filling Check & Backfilling
Unit No.
Grid Location or discription of area :
Activities / Items to be Ispected | [5 empty] | Status
[6 empty] | Remarks | Sign.
1 | Check proposed fill material has been tested and found complying specification requirement (Ref Lab testing report)
2 | Check Drawing No. and revision is current
Drwg No. - Rev.
3 | Check ground water level satisfactory
4 | Check necessary demarcation for base line and temporary bench mark (TBM) is established for reference level. Check base clean and free of stones and debris.
5 | Check availability of suitable compacting equipment and necessary level demarcation is made.
6 | Check that Anti-termite Treatment carried out as specified on drawings. (If applicable)
7 | Check water proofing to structures, if applicable is carried out as per spcification/vendor's approved procedure and testing is complete
8 | Check that protective coating to foundation is carried out and curring time is completed for same (where applicable)
9 | Check curing cycle of concrete structure is completed and all rectification/repair to concrete are carried out satisfactorily
10 | Check and ensure placement of fill in layer of 200mm max. and each layer is well compacted
11 | Check field compaction test where applicable was conducted and recorded . (Ref. compaction record format no. NJDBPL-2-QM00-FMT-CS-007).
Comments / Discrepancies :-
|  | N.J.Devani Builders Pvt.Ltd. | Reliance Construction Engineer |  | Reliance O&M/TPI
Signature
Name
Date
Format No. EPCMD-2QMOOFMTCS004, Rev.01 Date 27.10.2012
Page 1 of 1

## EXCAVATION & BASE
Excavation And Base Confirmation Record
Report No. : |  |  |  | Date :
Location of Excavation :
(attach marked-up copy of location drawing)
Activities / Items to be Inspected |  |  |  |  | Status
[5 empty] | Accept | Def.
1 | Verify that pre-excavation checks on Form NJDBPL-2QMOOFMTCS002 have been carried out and completed prior to start of job
2 | Record Drawing No. and check revision is current
Drwg No. - Rev.
3 | Excavated pit checked for dimension, cordinates and levels.
4 | Proof rolling is applicable is complete in accordance with specification.
5 | Check ground water level, and disopsal is required
6 | All Unsuitable, looze & foreign material removed
7 | Check foundation base is firm, as per specified zone |  |  |  | Zone :
8 | Check that base compaction test is carried out if applicable & test results meet requirements
(Testing format No. NJDBPL 2QMOOFMTCS021)
9 | Make necessary arrangement for shoring and ground support (If required)
Comments :
|  | N.J.Devani Builders Pvt.Ltd. | Reliance Construction Engineer |  | Reliance O&M/TPI
Signature
Name
Date
Format No. EPCMD-2QMOOFMTCS003, Rev.01 Date 30.11.2012
Page 1 of 1

## PRE-EXCAVATION
Pre-Excavation Checklist
Report No. : |  |  |  | Date :
Location of Area to be Excavated :
(attach marked-up copy of location drawing)
Activities / Items to be Checked |  |  |  |  | N.J.Devani | Client
1 | Latest Construction drawing
Drwg No. - Rev.
2 | Setting-out of survey and levels/TBM (Temporary Bench Mark) established as per drawing
3 | Necessary soil investigation carried out for soil strata
4 | Site clearance complete (If needed)
5 | Stockpile/ disposal area and haul roads established
6 | Excavated area and relevant drawings checked for existing underground utilities/obstructions, etc All identified utilities are suitably staked out on site.
7 | Ground water level checked and ground water control plan has been developed & approved
8 | Safe slope / ground support plan established, confirming that there is no effect on adjacent works.
Comments :
|  | N.J.Devani Builders Pvt.Ltd. | Reliance Construction Engineer |  | Reliance O&M/TPI
Signature
Name
Date
Format No. EPCMD-2QMOOFMTCS002, Rev.01 Date 30.11.2012
Page 1 of 1